## Wall U Values
Wall Section | Heat Flow [W] | Length [m] | Delta T [K] | Uvalue [Watts/m2-K] | Rvalue [m2-K/Watts] | Notes
K-Wall South Corner | 7.3714 | 0.898 | 39 | 0.21048 | 4.7511 | K-Wall refers to East Wall
K-Wall North Corner | 8.1256 | 0.888 | 39 | 0.23463 | 4.2621 | K-Wall refers to East Wall
K-Wall Middle Section | 12.6045 | 2.438 | 39 | 0.13256 | 7.5435 | K-Wall refers to East Wall
J-Wall South Corner | 7.1593 | 0.717 | 39 | 0.25603 | 3.9058 | J-Wall refers to Wall between Zone A and B
J-Wall North Corner | 0.8764 | 0.706 | 11 | 0.11285 | 8.8613 | J-Wall refers to Wall between Zone A and B
J-Wall Middle Section | 0.2363 | 0.236 | 11 | 0.091025 | 10.986 | J-Wall refers to Wall between Zone A and B
H-Wall South Corner | 4.7179 | 0.72 | 39 | 0.16802 | 5.9518 | H-Wall refers to Wall between Zone A and X2
H-Wall North Corner | 14.21 | 2.134 | 39 | 0.17074 | 5.8569 | H-Wall refers to Wall between Zone A and X2
H-Wall Middle Section | 0.1859 | 0.271 | 11 | 0.062362 | 16.0355 | H-Wall refers to Wall between Zone A and X2
South Wall Middle Section | 15.51 | 0.905 | 39 | 0.43944 | 2.2756
North Wall (N2-N3) | 10.6946 | 0.725 | 39 | 0.37824 | 2.6439 | see Drawing in sheet "North Wall Drawing"
North Wall (N4-N5) | 7.2934 | 1.57 | 39 | 0.11911 | 8.3953 | see Drawing in sheet "North Wall Drawing"
North Wall (N6-N7) | 8.6084 | 0.542 | 11 | 1.4439 | 0.69258 | see Drawing in sheet "North Wall Drawing"

## North Wall Drawing
N1
K-Wall North Corner (0.65m)
N2
Door Wall
<23> (1.37m)
N7
Int Door Head Wall (1.22 m)
N8
J-Wall North Corner (0.36 m)
N6
<19> (0.827m)
N3 Door Wall <23> (0.89 m)
N4 & N5 <16> & 7/A8.03 (1.45m)

## For report
Wall Section | Heat Flow [W] | Length [m] | Delta T [K] | Uvalue [Watts/m2-K] | Rvalue [m2-K/Watts] | Uvalue [Btu/hr-ft2-F] | Rvalue [Hr-ft2-F/Btu]
K-Wall South Corner | 7.37 | 0.898 | 39 | 0.21044 | 4.752 | 0.037062 | 26.9817
K-Wall North Corner | 8.1256 | 0.888 | 39 | 0.23463 | 4.2621 | 0.041322 | 24.2001
K-Wall Middle Section | 12.6045 | 2.438 | 39 | 0.13256 | 7.5435 | 0.023347 | 42.832
J-Wall South Corner | 3.61 | 0.717 | 39 | 0.1291 | 7.746 | 0.022737 | 43.9817
J-Wall North Corner | 0.096 | 0.706 | 1 | 0.13598 | 7.3542 | 0.023948 | 41.757
J-Wall Middle Section | 0.0215 | 0.236 | 1 | 0.091102 | 10.9767 | 0.016045 | 62.326
H-Wall South Corner | 4.1217 | 0.72 | 39 | 0.14678 | 6.8127 | 0.025851 | 38.6826
H-Wall North Corner | 14.6936 | 2.134 | 39 | 0.17655 | 5.6641 | 0.031094 | 32.1608
H-Wall Middle Section | 0.1859 | 0.271 | 11 | 0.062362 | 16.0355 | 0.010983 | 91.0496
South Wall (Window Wall) | 17.59 | 0.905 | 39 | 0.49837 | 2.0065 | 0.087772 | 11.3931
North Wall - Exterior Door Wall Section | 12.05 | 0.725 | 39 | 0.42617 | 2.3465 | 0.075057 | 13.3233
North Wall adjacent to the Electrical Room | 6.25 | 1.57 | 39 | 0.10207 | 9.7968 | 0.017977 | 55.6262
North Wall Adjacent to the Mechanical Room | 0.7733 | 0.542 | 1 | 1.4268 | 0.70089 | 0.25128 | 3.9797